## LIFT
BILL OF QUANTITY FOR SUPPLY & INSTALATION OF LIFTS OFFICE BUILDING
AT PuVVNL PREMISES AT BHELUPUR, VARANASI.
Sl. No. | Name of item of work |  | UNIT | QUANTITY | To be quoted the tenderer
[5 empty] | RATE | AMOUNT
1 | Supply/Design/Instalation/Testing and commissioning of lifts as per specification enclosed along with AUTO RESCUE DEVICE including all accessories, labour, material, T&P required for proper completion of the work up to satisfaction of Engineer-In-Charge including two year maintenance suitable for :-
| A | 13 No. Persons | No. | 01
| B | 13 No. Persons | No. | 01
List of makes as specified below :- OTIS/KONE/SCHINDLER/MITSUBISHI/JOHNSON/ECE
TOTAL
| J.E. |  | S.D.O |  |  | E.E
|  | NAME& FULL ADDRESS | ……………………………………………………….
……………………………………………………….
………………………………………………………….
………………………………………………………..
TENDER FOR SUPPLY & INSTALATION OF LIFTS OFFICE BUILDING
AT PuVVNL PREMISES AT BHELUPUR, VARANASI.
1 |  | WORK TO BE EXECUTED AS PER TENDER AND STATUTORY REGULATIONS ETC.
1.1 |  | Tender Document
This tender document, comprising of Notice Inviting Tender, Special Condition of Contract, Technical Specification, Schedule and Tender drawing etc. shall from part of the contract Agreement after award of contract. Work under this contract shall be executed at contract rate as per conditions and specifications stipulated in this tender document excepting in respect of deviation specifically agreed to before the awarded of the contract and in corporated in the contract Agreement In addition, components/ materials, which may not be specifically stipulated in the tender document, but which are necessary for satisfactory installation and/or operation of portion of work shall also be provided within the contract rates without my extra cost. Contractor shall carry out and complete the work in all respects to the satisfaction of Engineer-In-Charge/Architects.
1.2 |  | Tender Conditions, Specifications and Schedule
Provisions in Special Conditions of Contract shall be read in conjection with the Terms and Conditions of the Contract, Technical Specifications, Schedule of Quantities, Tender Drawing and any other document formating part of this contract Agreement.
For any discrepancy between the Terms and Conditions Contract and Special Conditions of Contract, provisions of special conditions of contract shall prevail.
For any discrepancy between Technical Specifications and Schedule of Quantities provision of Schedule of contract shall prevail.
Any item shown in Schedule of Quantities and not called for in the Specifications or vice versa, shall be provide as if called for in both.
Wherever it is mentioned that the Contractor shall perform certain work or provide certain facilities, it is understood that the Contractor shall do so at his cost.
Where the Technical Specifications stipulate requirements in addition to those contained in the applicable Indian Standard Specifications/Codes, these additional requirements shall also be satisfied.
1.3 |  | Authorities
The work shall conform to provisions of the relevant legislations, regulations and bye laws of the Central/Local Authorities and of the concerned Electricity Supply Authority. The contractor shall also be responsible for giving all notices required under the said Acts/Regulations/Bye-laws.
J.E. S.D.O. E.E.
TENDER FOR SUPPLY & INSTALATION OF LIFTS OFFICE BUILDING
AT PuVVNL PREMISES AT BHELUPUR, VARANASI.
1.4 |  | Electrical Lisence
The tenderers shall be licensed electrical Contractor processing a valid contractor's license of appropriate class in the state, employing licensed supervisors and skilled worker having valid permits as per the regulations of Indian Electricity rules and local Electrical Inspectors requirement. Copy of contractors Electrical license shall be furnished along with the Tender.
2 |  | INTENT OF SPECIFICATIONS It is not intent of Technical Specifications to completely specify all aspects of design/ construction features of equipments and all details of work to be carried out Nevertheless the intent of the Technical Specification is to ensure that the equipment and the work shall fully comply with and conform to the relevant Bureau of Indian Standard Specifications, Codes of Practice, Indian Electricity Act, Indian Electricity Rules and other Stautory Regulations, and other standards as may be applicable and to the best available standards of engineering, design and workmanship.The equipment and work shall perform in manner accepted to owners who shall interpret meaning of the applicable Specifications /Codes and shall have the right to reject any equipment or work, which in their assessment is not complete to meet the Standard /Code.
3 |  | SITE OF WORK
3.1 |  | Brief description of site Work covered in this contract is required for office building at Puvvnl premises at BHELUPUR, Varanasi. Tenderes are advised to visit the site after taking prior permission from Owners/Architects for familiarizing themselves with working conditions avilable at site as also with the statuory levies and their prevailing quantum payable at site . Contractors shall not be entiled to claim any extra payment on account of lack of such knowledge after award of contract.
3.2 |  | Power Supply System Entire work shall be suitable for use on 415 volt 3 phase 4 wire supply system with transformer neutral grounded.The rated frequency of the supply system shall be 50 cycles per second.
3.3 |  | Ambient Conditions All equipment components and materials used in the work shall be suitable for continuous operation/use at rated output with permissible overload over the entire range between the following extremes of ambient conditions likely to be encountered at site. Temperature from minimum 0˚C to maximum 50˚C Related humidity from minimum 10% RH to maximum 100% RH
4 |  | OWNER TO PROVIDE Owner's scope of contract shall be restricted to providing the following items free of cost to the contractor
Elevator hoiseway ( with structural openings for doors), Pit and Machine Room.
Space only for Contractor's site office/stores for the contract at location and of size considered suitable and seperable by owners. Owners reserve the right to provide alternative space for the purpose, if so necessary, during the tenure of the contract.
5 |  | SCOPE OF CONTRACT Contractor's scope of the contract shall comprise of providing all equipment, components, materials, fixing materials, accessories, labour, supervisory staff with infractucture, T&P, scaffolding consumable, testing equimpent etc. required for full and entire execution, testing,balancing, commissioning and completion of work called for in the item and as specifications and drawing and free comprensive maintenance for 2 (two) years after completion. Contract rates shall be deemed to be inclusive of all direct and indirect expenses required to be incurred as per this scope including but not restricted to the costs of the following.
5.1 |  | Contractualy Responsibility The Contractor shall be fully responsible for ensuring that the design, manufacture, make, type, quantity and size of equimpent/components/ materials brought to site for use in work shall be suitable for the work and shall be compaitible with spaces available at site particularly with regard to heights and the widths of approaches to place of installation of equimpent. Approval of shop drawings, makes, samples etc. given or on behalf of owenrs/ Architcts/Project Managers shall not absolve the contractor of this basic contractual responsibility.
5.2 |  | Items of work Design, manufacturing, supplying delivering to site, assembling fixing in position, connecting, testing, commissioning and leaving in working order, all necessary materials and equimpent including minor and incident works to ensure complete and satisfactory operation. This shall include interface work other M&E trades and condition with other Contractor working at the project site.
5.3 |  | Statutory levies
Prevailling Statuory levies shall be applicable.
Central Sales Tax without issue of C form by Owner
Excise /Costom duty
5.4 |  | Testing Testing for the various items of equimpent shall be performed at the contractor's cost and test certificate to be furnished by the contractor ( for Motor, Machine Break-tests controller & street wire Ropes). If required by the Engineer, the contractor shall permit toe owner's authorized representative to be present during any of the tests. After notification to the Owner that the installation has been completed the contractor shall make under the direction and in the presence of the Engineer such test and inspections as have been specified or as the Engineer shall consider necessary to determine whether or not the full intent of the requipments of the plans and specifications have been fulfilled. In case the work does not meet the full intent of the specificaions and further tests shall be considered necessay the contractor shall bear all the expenses there of.
5.5 |  | Transportation, Storage, insurance etc.
Loading, transportation and unloading
Protection of stored materials/installed work against due to dirt, sun and rain including providing rarpaulin/PVC sheet covers as required.
Providing security arrangements/ watch and ward for stored materials and installed works to guard against pilferage/damage.
Comprehensive insurance with owners as beneficiaries against pilferage/damage during transportation/storage/installation valid till handing over.
Third party insurance of adequate amount.
5.6 |  | Name plates & labels
Providing engraved anodized aluminium or approval equivalent name plates of suitable sizes on switchboards/panels/equipments etc.
5.7 |  | Civil works, cleaning and painting
5.71 |  | Civils works.
All steel items required for intallation and operation of elevator system in pits, Elevaor wells and machine rooms.
All civil work items required for the work including but not restricted to making chases in walls/ ceilings, making holes and openings, providing inserts, grouting etc including making good the same with wire mesh covering first and then cement mortar/concrete/water proofing of appropriate mix and strength as directed by the E/I, Maching paints shall applied on portions so made good.
Restoration of the fire resistive rating of the floor and wall assemblies by sealing all through penetrations made by conduits, cable, pipes etc. by sealing material (made avilable by ITC ) in accordance with manufactures instructions/specifications.
Any cable crossing fire rated wall as per fire compartmentalization shall be provided with higher size of GI sleeve. All floor crossing cables shall be provided with higher size GI sleeve.
| 5.72 | Housekeeping
Housekeeping and clearing of work area during the tenure of contract.
| 5.73 | Site Clearance
Demobilization and clearing of all temporary works/facelities after completion of work at site and clearing work are before handing over.
| 5.74 | Providing final paint coat to all exposed fabricated steel work and providing matching paint in approved manner over portions of factory painted equipment if damaged during transporttation/storage/installation before hoading over.
| 5.8 | Statutory approvals
Obtaining approval from Elevator Inspector and NOC from U.P. Govt. /Concerned Fire Service for satisfactory installation of the elevator system as also for clearance to put the elevators in to regular use.
Obtaining any other statutory permission/elearance/approval from concerned authority as required.
Pay any licensing fee/sumission fee/inspection fee payble to statutory authorties for obtaining above approvals.
| 5.9 | Compliance of statutory observation
Complying with observation if any, of Lift/Electrical Inspector and/or any other Statutory Authority after completion of work in order to obtain a categorical clearance to start beneficial use.
| 5.1 | Manuals, drawing etc.
| 5.10.1 | Along with the tender
Technical parameters enclosed as Amexure-I duly filled in by the tenders along with technical catalogues etc. of the equipment offered.
| 5.10.2 | Schedule of construction in the form of a PERT chart or Bar chart for Project Manager's approval. Shop drawings made on Auto CAD and coloured prints, coordinated with other trading works, shall incorporate elevator manufacturers details and dimensions to ensure that the same can be installed in the space provided. Facilities for proper maintenance, repair and replacement of the equimpent shall be clearly shown in the drawings. The contractor shall also ascertain that facilities provided by other agencies in the form of space, access, lighting, ventilation and the like proposed/provided are adequate. The shop drawings shall be got approved from the Engineer of the contract/Consultants befor undertaking manufacture/ fabrication/installation activites.
| 5.10.3 | Completion documents The Contractor shall submit completion document s comprising of the following at the time of handing over hard copies of operating instruction and Service manul along with CD for use by owners operating staff.
3 hard copies of operating Insturction & Service Manual along with.CD for use by Owners operating staff.
3 Sets of test results of pre-commissioning tests carried out at site.
3 sets of " As Built" GA drawings.
| 5.10.4 | Training Training of Owners personnel in operation, handing and maintenance of equipment.
| 5.10.5 | COMPLETION TIME & TIME DELAY PENALTY
| 5.10.5.1 | Completion
The entire work shall be completed with in 6 (Six) month from the issue of letter of intent. The contractor shall submit a bar chart along with the tender and a detailed time schedule of completing salient activities of the contract to achieve overall completion for approval of Architect /Owners. The Contractor shall ensure supply and erection of sill angles and door frames with in 2 months of issue of letter of intent or with in one month of handing over of lift shaft whichever is earlier to enable coordinated completion of terms like Archtiraves, facia returens in stone etc. by other agencies. If the completion of work is delayed beyond the period stipulated in the original contract agrement due to reasons considered by owners to beyond the control of Contractor, extension of time for the completion of the work shall be granted by the Owners without the levy of the time delay penalty. The extension of time shall however not e entile the contractor to claim any extra payment and/or compensation on this account.
Completion of work shall include supply, installation, testing, commissioning obtaining the required statutory approvals. The work shall not be demand to be completed till all these items are completed by the contractor to the satisfaction of the owner.
| 5.10.5.2 | Time delay Penalty
| 5.10.5.3 | Delay in final completion
If the completion of the work is delayed beyond the completion period stipulated in the contract agreement due to reasons considered by owners to be with in contract's control owners reserve the right to impose .Time Delay Penalty on the contractor @ 0.5% of the total contract value per week of delay subject to a maximum of 10% of the total contract value.
| 6 | GENERAL REQUIREMENTS
| 6.1 | Packing, storage and protection.
Any item suffering from damage during manufacture, or in transit, or in the whilst in storage or during erection shall be rejected and replaced without extension of time and extra cost to the employer.
The contrator shall also apply an approved protective crating or fix some other protective materials or measures to the materials, equipment components and accessories so as to protect them free dust, stains, moistures, debris, damage, etc after installation. In the even that the contractor fails to do this the contractor shall repair to the satisfaction of the architect or supply free of all charge any replacement required to substitute any part of the materials, equipment, components and accessories which may have been damaged in whole or in part as a result of such failure, as directed by the Architect and shall without prjudice to such other liabilites under this contraxt, pay for all expenses and outgoings of the Employer incurred in respect of the removal and disposal of the damaged parts and the installation of the substituted part.
The contractor shall also ensure that all plant and equipment are correctly maintained when installed on site prior to their actual setting to work. In particular, all major equipment shall have long term storage warrenty maintenance where by they are prepared for long term nonuse by the supplier/or his agent, and a programme of regular maintenance is to be included in the contract. This will include tuming of motors, activation of electrical heaters and the like. The details of the proper set works must be submitted with in 1 month after award of contract for approval.
The contractor shall be entirely responsible for all apparatus, equipment and materials furmished by him in connection with the works and special care shall be taken to protect all parts there four in such a manner as may necessary or as directed.
Protection shall include covers to prevent grit, plaster or other foregin substance from entering the working parts of machinery or equipment and special care shall be taken to keep all open ends of of pipes, conduties etc. closed white in storage or in the course or erection.
All materials and equipment supplied under the contract must be new, complete , intact and in good order, the use of reconditioned or used parts and equipment shall not be pemitted unless for items spacially mentioned.
The Contractor shall take precaution to avoid causing unnecssary damage to the work of other traders and, in particular, when installing heavy loads.
The Conctractor workmen will be required to conform with the general regulation goverming personnel on the site and must keep the working space allotted to the Contractor.
| 6.2 | Coordination with other agencies.
The elevator contractor shall be responsible to coordinate the work of elevator installation with other agencies working at site. The elevator contractor shall have to carry out changes/modifications, if any, required due to lack of coodrnation with other agencies at his cost.
| 6.3 | Site Surpervision The Contractor shall keep on site at all times while work is in progress an efficient supervisor, empowered receive and carry out instructions on site. The supervisior shall not be changed without prior approval of the engineer. A site draughtsman shall be kept on site to facilitate prompt issue of shop drawing. The name and qualifications of the site supervisor whom the Contractor proposes to appoint shall be submitted to the engineer prior to appointment and the engineer shall have the right to approve or reject the proposal.
The Contractor shall engage sufficient qualified and experenced site staff to execute the works. Registered and licensed tradespersons shall be employed under the direct employment of the contrat and shall be full time on site to supervise the works, if necessary. The architects decision as to what constututes this necessity shall be final and binding . When requested by the archiect, sufficient draghtsman shall be kept on site to faciliate prompt issue on shop drawings.
| 6.4 | Personal to be technically qualified
The Services of licensed electrical engineers, professional engineers ( mechanical and electrical) and suitably appropriate qualified licensed workser shall be engaged to assme full responsibilities for all engineering matters. These personnel shall be abvailable to attend meetings, discussions, inpection, and the like as requested by the Architect and for any activation of electrical equipment, switchboards and other equipment/systems. Upon completion of the contract works, the licensed electrical engineer and professional engineers shall furnish completion and inspection certificates for the respective parts of the works to the architect to cerfify that all the works in full compliance with the speciffications and drawings.
| 6.5 | Inspection at manufacturers works
Owners reserve the right to depute their representiative for inspection of the elevators and for witnessing tests at manufature's works prior to dispatch of the elevators to site.
| 6.6 | Completion certificate acceptance procedure
The contractor shall adherer to the sequence of operation and handover described below
a) The contractor shall submit the details of the commissioning engineers whose qualifications must be to the satisfaction of the architect/engineer. The architect/engineers reserves the right to reject any unsuitable person.
b) One completion of the electrical installation o certificate shall be furnished by the contractor counter signed by thelicensed supervisor under whose direct supervision the installation was carried out. The certificate shall be in the prescribed form as required by the local supply authority. The contractor shall be responsible for getting the electrical installation inspected and approved by the local and statutory authorities concened.
C) The Contractor shall also handover any special tools, keys etc. which are required for regular operation of the elevators.
| 6.7 | Maintenance
During the period that the maintenance is entrusted to the contractor, the contractor shall
Provide a 24 hour call out service whereby at any time the contractor shall dispatch skilled personnel to repair any equpment that has broken down.
Immeciately answering the breakdown calls, whether true or false the contractor shall attend to such clls within a maximum time limit of 2 hours of receiving such calls.
Remedy and make good with all possible speed any faults or defects in the plant or works in the opinion of the architect/engineer, due to fault materials, workmanship or design. The contractor shall indemnify the employer and /or the main contractor aainst any damage or injury to the building contents and/or occupants arising as a result of such faults or detects.
If the Contractor fails to remedy such faults or defects within a resonable time the employer may proceed to do so at the risk and expense of the contractor and without prejudice to such other rights as the employer may have under the contract.
| 6.8 | As new condition
At the time of handover of the contract works after the maintenane period the whole installation shall be in 'as-new' condition. The contractor shall during the course of the contract, prodect all plant and equipment and shall restore/repaint as necessary befor completion of the contract.
| 6.9 | Safety Aspects
Since elevtor installation consists o a number of electrical and mechanical components having linear /rotary motions, utmost caution should be exercised while working and all safety precautions shall be rigorously followed.
Only authorized persons shall be allowed to work on elevator installations and officer empowered for such authorization shall keep proper recorded there of during the test, inspection and maintenance except where necessary.
If during erection any safety or protection devices is inoperative, special care must be taken to avoid accidents on this account.
Supply at main incoming iron clad switch or circuit beaker shall be switched off before examining any part of the equipment .Wheather during periodical inspection or while carrying out any work on the equipments ( including using the winding handle at times of mains failutes) unless power is particularly required for particular operation or tests on the elevators. The braker located in OFF posittion.
Whenever the car needs to be moved by use of winding handle in the machine room
a) Power at incoming shall be switched off before applying the handle.
b) Power shall be restored only after this handle is removed from winding shaft and brakes are applied.
The handing and car buttons shall be keep out of circuity by switching on the 'Maintenance Switch' located on the top of the elevator car during maintenance operators. Whenever maintenance switch is not proved emergency stop swith inside car attendant control swith should be used.
Before carrying out any repair work it shall be ensured that more of the electro-mechanical door locks are short circuited either from the controller or at the leading.
As a general precation, facia plate between the door headers and the corresponding uper landing sill on each floor must be provided.
7 |  | FREE MAINTENANCE PERIODS
7.1 |  | Maintenance
Quoted rates shall be deemed to be inclusive of free comprehensive maintenance (including spares ) of lifts for period of Two year from the accepted date of completion of the contract.
| 8 | TERMS OF PAYMENT
The payments shall be released only after necessary submission/ checking of bills.
Income tax, Sale tax & Service tax (as applicable) shall be deducts from Contractor bills as per rules prevailing during the currency of the contract.
| 9 | PERFORMANCE GUARANTEE
Immediately after award of work the contractor shall submit a performance guarantee equivalent to 10% of contract value from a nationalized /Scheduled bank on our approved proforma. The performance guarantee shall be effiective from the date of commencment of the work upt to the completion of free maintenance period.
| 10 | TAXES/DUTIES
All sales tax/excise duty or any other taxes or levies including salex tax on works contract payble to any authorities whatsoever shall be bome by contractor and Employer/Consultants accept no responsibility or liability whatsover on any account. Component of excise duty and sales tax shall be indicated separetly. Any fresh taxes levied during the corrency of the contract shall be payable by the employer.
| 11 | TAX DEDUCTION AT SOURCE
Income tax and sale tax shall be deduced from the running bills as per statutory requirements.
| 12 | FINAL BILL
The payments of final bill duty certified by the Employer's Engineer shall be made with in 3 (three) months of receipt of bill after effecting due, recoveries and deductions.
| 13 | WATER AND ELECTRICITY
a) Water shall be supplied of cost by the owner at one point only.Any further distribution as required shall be the responbility of the contractor at his own cost. The supplies shall be limited to the time and quantum supply by Municipal Aothority.
b) The Contractor shall make his own arrangements for electricity at site. Nothing extra shall be payble for this.
| 14 | GODOWN/ WORKER ACCOMMODATION
The accommodation for works shall be arranged by the Contractor, No. labour hutments shall be allowed within the site premises. Storage space shall be arranged by the owner's contractor shall construct the stores at his cost and he shall be responsible for watch and ward of his materials/ installation.
| 15 | MINOR CIVIL WORKS
Minor Civil works such as cutting holes and making good for hall buttons, indicators including laying of sill in position and providing dash fasteners for fixing car and counter weight, rail brackets shall be bome by contractors at his own cost.
| 16 | CONTRACT PRICE
Rates quoted shall hold good for any increase /decrease in the quantities. Any of the items may be deleted as per dirctions of Owner/Achitect. In respect of any additional item ordered to be executed, the rates payable shall be derived from market, rates, supporting vouchers plus10% will be added there on for Contractors profit and overhead.
| 17 | TENDER ACCEPTANCE
The owner reserve the right to award the contract to any bidder other than lowest without assigning any reason what so ever.
| 18 | SAFETY REGULATIONS
The Contractors shall at their own expense, arrange for safety provisions as per safety dodes of Indian Standards Institution, Indian Electricity Act and such other Rules, Regulations and Laws as may be applicable as indicated below, in respect of all labour, directly or indirectly employed in the work for performance of the contractor's part of this agreement.
No inflammable materials shall be stored in place other than the rooms specially constructed for this purposes in accordance with the provisions of Indian Explosives Act. If such stroage is unavoidable, it should be allowed only for a short period and in addition, special precautions such as cutting off the supply to such places at normal items, storing materials away form wring and switch boards, giving electric supply for temporary period with due premission of Engineer-in-charge shall be taken.
Protective and safety equipment such as rubber gauntles or gloves, earthing rols line men's belt, portable artificial respiration apparatus atc. Shoud be provided in easily identifiable locations. Where electric welding or such other nature of work is undertaken, goggles shall also be provided.
All necessary personal safety equipment such as Helmets, Protective footwear protective goggles/ eye shields, Life jacket, Gas maks etc, as considered adequate by the E/I. shall be available for use of persons employed on the site and maintained in a conditions suitable for immediate use and the contractor shall take adequate steps to ensure proper use of equimpent by those concerned.
Safety means of access shall be provided to all working platforms and other working places. Every ladder shall be securely fixed. Adequate precautions shall be taken to prevent danger from electrical equipment .
The Contractor shall provide all necessary fencing and lights to protect public from accidents and shall be bound to bear expenses of defence of every sut, action or other proceeding at law that may be brought by any person for injurry sustained owning to neglect of the above pecautions and to pay any demages and costs which may be awarded in any such suit, action or proceedings to any such person or which may with the consent of the contractor be paid to compromise any claim by any such person or which may with the consent of the contractor by paid to compromise any claim by any such person.
Motor gearing , transmission, electric wring and other damgerous parts of hoisting appliances shall be provided with efficient safe guards; hoisting applicne shall be provided with such means as will reduce to the minimum risk of accidental descend of load. Adepuate precations shall be taken to reduce to the miniumum risk of any part of a suspended load to compromise any claim by any such person.
All scaffolds, ladders, First Aid Equipments/medicines and other safety devices shall be maintained in a safe condition and no scaffold, ladder or equipment shall be altered or removed while it is in use. Adequate washing facilities shall be provided at or near place of work.necessary warning sign boards in Red/White paint, with proper lighting arrangement for nights are to be provided at prominent locations.
Necessary number of caution such as "Man on Line,Don't switchm on" should by readily available in easily indenifiable locations.
Standard first aid boxes containing materials as prescribed by the St. John Ambulance Brigade of Indian Red Cross should be provided in easily identifiable location and should be readily avilable. Periodical examination of the firs taid faclities and protective and safety equipment provided shall be undertaken and proper records shall be maintained for their adequacy and effectiveness.
Charts ( one in Engilsh and one in regional lenguage) displaying methods of living artificial respiration to a recipient of electrical shock, shall be prominently displyed at appropriate place.
A chart containing the names, addresses and telephone numbers of nearest authorized medical practioners, hospital, Fire, Brigade and also of the officers in charge shall be displayed prominetly alongwith the First Aid Box.
Steps to train supervisory and authorized persons of the Engineering staff in the First Aid practices, including various methods of artificial respiration with the help of local authorties such as Fire Brigade. St. John's Ambulace Brigade, India Red Cross or other recognized equipped to impart such training shall be taken. as prompt redering of artifical respiration can save life at time of electric shock.
No work shall be undertaken on live installation or on installation which could energized unless one another person is respect to immediately isolate the electric supply in case of any accident and to render first aid, if necessary.
| 19 | COMPLETION CERTIFICATE
One completion of the electrical installastion a certificate shall be furnished by the Contractor countesigned by the Licensed Supervisor, under whose direct supervision the installation was carried out. This certificate shall be in the prescribed form as required by the local supply aothority. the contractor shall be in the responsible for getting the elecrtical installation inspected and approved by the local and statutory authorities concerned, and if expenses if any shall be bome by the contractors.
| 20 | WORKMANSHIP
Good workmanship is an essential prerequisite to be complied for this work. Entire work shall be carried out in the most workmanlike manner by skilled workers under competent superision.
TENDER FOR SUPPLY & INSTALATION OF LIFTS OFFOCE BUILDING
AT PuVVNL PREMISES AT BHELUPUR, VARANASI.
SPECIAL CONDITIONS OF CONTRACT
TECHNICAL SPECIFICATIONS
| 1 | STANDARDS
The following BIS Standards and codes of Pratice with up to date amendments shall apply to the equipment and the work covered by this contract.
Electric Traction Lifts-Guide line for outline dimension of
|  | Passenger, goods, Service and Hospital Lifts |  |  | IS 14665 (Part-I)-2000
|  | Electric Traction Lifts-Code of practice for installation |  |  | IS 14665 (Part-2)-2000
|  | Electric Traction Lifts- Safety Rules |  |  | IS 14665 (Part-3)-2000
|  | Electric Traction Lifts- Components |  |  | IS 14665 (Part-3)-2000
|  | Code of practice for electrcal wiring installation (System voltage not exceeding 650 volts) |  |  | IS 732-1963
In addition the relevant clauses of the following as amended up to date shall apply.
(a) The Indian Elecrticity Rules 1956
(b) The Indian Elecrticity Act 1910
(c) Bombay Lift Act 1939
(d) Delhi /Concerned Lift Rules
The tenderdrs shall also take in to account local and State regulations as in vogue for the design and installation of lifts.
Wherever appropriate Indian Standards are not availble, relevant British and /or IEC standard shall be applicable BIS certified equipment shall be used as part of the Contract.
| 2 | TECHNICAL PARAMETERS
Technical parameters given in Annexure-I give requirement of various parameters as per tender. Tenderers shall fill in their itemwise confirmation/comments in the colum provided for the purpose in thisannexure, Deviation, if any, from tender requirements shall be clearly brought out in this annexure, failing which it shall be presumed that the offer conforms to the tender requirements fully. Tenders in which Annexure-I is not duly filled in by the tenders are liable to be summarily rejected.
| 3 | DRIVING MECHANISM
| 3.1 | Lift Machine
The lift machine shall be suitable for 415 volt 3 phase 50Hz AC supply with a volatge variation of +10% and-20% and shall be placed directed above the hoistway on steel beams resting on machine room floor slab.
The lift machine shall be efficiency and low power consumption and shall be designed to withstand peak currents in lift duties. Reslient anti vibration mountings of suitable design shall be provided to minimize vibration transmission to the building structure.
The lift machine shall be worm geared reduction type and shall consist of a motor, electromechanical brake worm-gear, sheve shaft and sheve all completely mounted on a common bed plat. The worm shall be provided with ball earings to take the end thrust and roller bearings shall provided for the sheve shaft to ensure aligment and long bearing life. The hard alloy cast iron or steel sheve shall have rope grooves to ensure proper traction and minimum rope wear. Adequate means of lubrication shall be provided for all bearings and work gear.
Means for manual operation of the lift car shall be made by providing winding wheel suitably marked to incicate the direction of the movement to enable the lift car to be brought to the nearest landing. There shall be a warning display for switching off electrical supply befor the manual operations.
| 3.2 | Brake
The electromagnetic brake shall be spring applied and electrically released. It shall come in to action after the lift has come to a complete halt to hold the car in position. The brake shall operate automatically with the safety devices and failure of the mains. It shall be released electrically. It shall be possibe to release the brake manually-such release requiring the action of manual force to move the lift in short stops.
| 3.3 | AC Motor
The AC self lubricating motor shall be suitable for lift use with ligh starting forque and low starting current. Thermistors shall be embedded in the stator windings to indicate the temperature rise in the motor. The AC motor shall have class F insulation and suitable for 180 starts per hour with a maximum temperature rise of 45 degree C over th ambient.
| 4 | CONTROL
The Lifts shall have state of art microprocessor based AC Variable Voltage Variable Frequency (ACVVVF) drive. The contractor should use distributed computing power to provide powerful Group Control features which help meet the Traffice needs for Mid Rise building like Waiting time optmisation, Dynamic call allocation, sudden peak detection, Express service priority landings, Radundancy, Parking of the free lift, Cancel of false slls, Cancel of calls in opposite direction, Misuse of landing calls, Door open time Soecial function floors etc. complete details of these features shall be fumished along with the tender.
The controller shall be wall/floor mounted, vertical, totally enclosed cubicle type with hinged doors on the front and the reat to provide easy access to all components in the controller. The cubicle shall be well ventilated such that the temperature inside never exceeds the safe limits of the components at ambient room conditions in the machince room.
The controller shall operate with in the supply voltage variation of plus 10% to minus 20% of the norminal voltage.
The Controller shll be complete with relay protection against the following:
a) Overcurrent
b) Under voltage
c) Over voltage
d) Single phasing
e) Phase reversal
f) Earth leakage
The controller shall be designed to cut power supply, apply the break and bring the car to a rest in the event of any of the above failures occruing .
The tenderer shall state clearly the forms of protection provided for each equipment.
If any devices of the eletro mechanical type are used the same shall be equipment with are chutes to prolong the life of contract. Tenderers shall stipulate the type of devices used and the material of the contacts.
Tenderers shall support their offers with complete details of experience, number of lifts installed and operational in India, collaboration for equipment desigbn and manufacture etc.
| 5 | COUNTER WEIGHT
The counter weight shall be made of cast iron and shall travel between rigid guides and steel frames capable of withstandaing buffer impacts. Suitable metalic counter weight guard of required length shall be provided at the bottom of the hoistway.
| 6 | GUIDEs
Car and cournterweight guide shall be machinaed T section as per relevant India Standards IS -4666-1968 revised up to date. The guides shall be capable of withstanding forces resulting from the application of the car or counter weight safety devices.
| 7 | HOIST ROPES
Round standard steel wire ropes as per Indian Standards shall be used for lift suspension. The number and size of the hoistway ropes shall be so selected to ensure proper factor of safety( minumum 10) and adequate traction for the lift. The governor ropes shall also be wire ropes.
| 8 | DOORS
| 8.1 | Car & Hoistway Door Protection.
The equipment shall be complete with electric door operator for opening and closing of Car & Hoistway Inding door. The equipment shall consist of a motor on the lift car to operate the door when the car is stoopping at a landing. The car & Hoistway doors shall be mechnically connected such that both move simultaaneously for opening and closing.
The Hostway landing door shall be provided with an interlock such that:
| a) | It shall not be possibe for the car to be started or kept in motion until all the landing doors and the car door are locked in the closed position.
| b) | It shall not be possibe to open the landing door from the landing unless the lift car is within the particular landing zone.
| c) | The car doors & Hoistway landing doors open automancically as the car is stopping at a landing .The closing of the car and landing door must occur before the car is set in motion.
| 8.3 | Door Hangers and Tracks
The car and the landing doors shall be provided with two point suspension sheave type hangers complete with tracks. Sheaves and rollers shall be steel with moulded mylon collar and shall include shielded ball bearings. Tracks shall be of suitable steel section with smooth surface. The landing doors shall be complete with headers, sills, frames etc. as required.
| 9 | CABIN FAN
A noiseless blower fan shall be provided in the cabin.
| 10 | EMERGENCY LIGHT
An emergency light unit using sealed Nicke/Cadmium maintenance free battery power pack with chargr and fluorecoent lamp to operate automatically and to illuminate the car for minimum 30 minuts in case of power failure shall be provided each lift car.
| 11 | ALARM BELL
An emergency alarm bell, including wiring shall be provided and connected to a plainly marked push button in the car operating panel. The alarm shall be located in the control and the security room.
The alarm unit shall be solid-state siren type, operated by Nicket/Cadmium maintenance free batteries to give waxing and waning siren when the alarm button in the car is pressed momentarly.
| 12 | DIGITALIZED VOICE SYNTHESIZER
The following operation buttons and indications shall be provided:
| 13.1 | In each Lift Car
Stainless steel panel of suitble thickness flush mounted shall be provided on one side of the door having:
a) LED Illuninted push buttons of micro pressure type corresponding to the floors served.
b) Door open button
c) Emergency stop button
d)Emergency alarm button
e)Two position key operated switch for 'with attendant' and 'without attendant' operation.
f) Ventilation fan ON/OFF switch with auto OFF when there is no call after 120 seconds.
g) Built in intercom of the hands free type.
h) Dynamic car direction display
i) Car position indicator
j) Audio/Visual overload warning indicator
k) Digital voice synthesizer for amouncing special messages on energy conservation of predetermined level with background music.
| 13.2 | At Landings:
Terminal landings
LED Illuminated type single push butttons with travel indication arrow in satin finish stainless steel facia plate.
Digital car position indicator with gong in stainless steel facia plate.
Intermediate Landings
LED Illuminated type push butttons with travel indication arrow in satin finish stainless steel facia plate.
Digital car position indicator with gong in stainless steel facia plate.
| 14 | SAFETY DEVICES
All safety devices statutorily required by Lift Inspector, including but not restricted to the following shall be provided.
| 14.1 | Self Leveling
The Lifts shall be provided with self leveling features of ±3 mm accuracy.
| 14.2 | Terminal and Final Limits.
Terminal limit switch shall be provided to slow down and stop the car automatically at the terminal landings and final limit switches shall be furnished to automatically cut off power should the car travel beyond the terminal landings.
| 14.3 | Terminal Bufers
Suitable spring buffers shall be installed mounted on steel channels as a means of stopping the car
| 14.4 | Interlocking
Adequate interlocking is to be provided so that the car shall not move if the landing doors are even partially open and also the lift is overloaded.
| 14.5 | Car Safety and Governor
The car safety shall be provided to stop the car whenever excessive desceding speed is attained.
| 14.6 | Emergency Stop Switches
An emergency stop for use maintenance personal shall be provided in each lift car.
| 15 | ASSOCIATED CIVIL & STRUCTURAL ITEMS
All civil and structural items of work associated with erection and operation of lift shall be provided by the Contractor at his cost including ( but not restricted to ) the following.
(a) Temporary Scaffolding and safety barricades during lift installation in and around lift hoist ways.
(b) Bearing plates
(c ) Buffer supports
(d) Checqured plates
(e) Facia plates
(f) Ladder in pits
(g) Safety railing in car
(h) Channels, separators, strtchers etc.
(i) Breaking, fixing and making good spaces for leveling switches and any other erecion work.
Lifting hook embedded in machine room roof slab in the enter of the hoistway shall be provided by Owners.
The Contractor shall ensure erection and fixing of steel work in such a manner that no RCC wall or any other structural member is damaged and if damaged, the contractor shall be responsible for making good the damage to original finish.
| 16 | FIREMAN SWITCH
Each independent lift and one per a group shall have a Fireman switch with galss front for access by the Firemen. The operation of this switch shall cancel all calls to this lift and will stop at the next nearest landing if traveling upwards. The doors witll not open at this landing and the lift witll return to the ground floor. In case the lift is traveling downwards when the fireman's switch is operated it will go straight to the ground floor bypasing all calls enroute. The emergency stop button inside the car shall be redered inoperative.
|  | J.E. | S.D.O. |  |  | Ex.Eng.

## PART OF LIFT
TENDER FOR SUPPLY & INSTALATION OF LIFTS OFFICE BUILDING
AT PuVVNL PREMISES AT BHELUPUR, VARANASI.
SPECIAL CONDITIONS OF CONTRACT
TECHNICAL PARAMETERS
ANNEXURE-I
Note:
Tenderers to give item wise confirmation/comment against each parameter. Deviations if any shall be clearly brought out in this performa. Tenderers shall fill in the performa and enclose it along with the tender
Sl.Nl. | Items | Requirement as per tender | Item wise confirmation / comment to be filled in by tenderers.
A | PASSENGER LIFTS
General
1.1 | Number of Lifts | Total-2Nos.
1.2 | Capacity | 1No.-13 Passenger (884kg)
1No.-13 Passenger (884kg)
1.3 | Speed | 1.0 mps
1.4 | Number of Landings | 4 stops (Ground to 3rd floor)
1.5 | Numder of Opening | 4 Opening ( all opening) the same side
1.6 | Travel | 12.00 (approx)
Machine, Hoistway and pit
1.7 | Machine room location | directly above Hosistway
1.8 | Machine details | 415 volts, 3 phase, 50, 1+2 A.C.
| Control | Micro Poocessor band V.V.V.F. ARD SYSTEM
| Operation | Microprocessor
1.9 | Hoistway dimensions
| Width ( along door) | Lift (10P) = 1900mm
| Deep (90˚ to door) | Lift (10P) = 2100mm
1.1 | Head room above last landing | Lift (10P) =4800mm Lift (8P) =4800mm
1.11 | Pit depth | Lift (10P) =1600mm Lift
1.12 | Sill Projection | M.S. Angle
| Jr. Engr. | S.D.O | Ex.Eng.
Car
1.13 | Car Enclosure | SS CABIN HAIR LINE FINISH
1.14 | Car ceiling | Stainless steel Hair line false ceiling with pressure fan and sufficient no. of CFL light fittings.
1.15 | Car floor | Car flooring shall have a recess of 25mm to accommodate stone tile finish to be provided by Owners through other agencies.
1.16 | Car and landing doors | Proted by center opening hair …..
1.17 | Car size | 1500mm wide x1470mm x2300mm deep
1.18 | Door of lifts | 900mx2100
1.19 | Car height of lifts | 2300mm
| Jr. Engr. | S.D.O | Ex.Eng.
Sl.Nl. | Items | Requirement as per tender | Item wise confirmation / comment to be filled in by tenderers.
B | PARAMETERS COMMON TO ALL LIFTS
1 | Machine
1.1 | Power Supply | 415V/240V,50HZ
1.2 | Acceptable voltage fluctuation | $10 to &20%
1.3 | Rate of acceleration / declaration m/sec2) | 0.6-1.5 (adjustable at site)
1.4 | Jerk (m/sec2) | 0.7-1.5 (adjustable at site)
1.5 | Vibration in car horizontal /vertical | 20 /18 dBA maximum
1.6 | Noise level in car | 48dBA maximum
1.7 | Noise level in machine room at 1 mtr from machine | 62dBA maximum
1.8 | Door noise level while closing and opening at distance of 1 mtr from at car door and 1.5 mtr from floor level. | 52dBA maximum
2 | Fixtures/signals inside car
2.1 | Hand rail | Provision to be made for fixing of hand rails.
2.2 | Normal lighting | CFL recessed type
2.3 | Emergency light and alarm bell ( to security room) | With SMF battery operated with charge rated for 30 minute
2.4 | Ventilation | Blower Fan
2.5 | Operating buttons and indications | Stainless steel operating panel with following buttons and indications. LED illuminated push buttons of micro pressure type corresponding to the floors served.
Door open button
Emergency stop button
Emergency alarm button
Two position key operated switch for 'with attendant' and 'without attendant' operation.
Ventilation fan ON/OFF switch with auto OFF when there is no call after 120 seconds.
Built in intercom of the hands free type.
Dynamic car direction display
Digital Car position indicator
Visual overload warming indicator
2.6 | Music | Trailing cable
2.7 | Voice Synthesizer | To be quoted as optional extra
3 | Landing Signals
3.1 | Hall buttons | Self illuminating micro-push type in hari line stainless steel facia plates.
3.2 | Car Position | Degital incicator with direction of travel
3.3 | Hall gong | Up/down indicator with single strok gong/chine at all landing.
4 | BMS interface | Potential free contacts for linking with BMS for
Lift position
Lift derection
Lift not working/lift under breakdown.
Parking of Lift at desired floor
Note; Contractor to provided diagrammatical representation of interface provision for BMS and the provisions made in the controller.
5 | Safetu featires
5.1 | Door safety | Infrared/Electronic detectors
5.2 | Buffer | Spring Buffer to be provided
5.3 | Overload protection | Overload protective device Overload non stater
5.4 | Over travel protection | Terminal and final limit switches to be provided
5.5 | Motor protection | Trip devices for: Over current Under voltage Over voltage Single plasing Earth leakage Phase reversal
5.6 | Interlocking of car and hoiwtway doors | To be provided as per specification:
5.7 | Auto Rescue Device (ARD) | To be provided as per norm.
6 | Associated Civil and structural items | All civil and structural items of work associated with erection and operation of lift shall be provided by the contractor at his cost including (but not restricted to ) the following:
Temporary Scaffolding and safety barricades for erection in and around lift hoist ways
Bearing plates
Buffer supports
Checqured plates (for service lift only)
Facia plates
Safety railing on top car
Channels, separators, stretchers etc.
Ladder in pit
Sill angles
7 | Fireman's Switch | To be provided at GF/Lobby level
8 | Free Comprehensive Maintenance Period | TWO YEARS After completion of work and handing over of the Lifts in satisfactory operating conditions.
SPECIAL DATA TO BE FURNISHED BY TENDERERS
Sl. No. | Data to be filled in by tenderers | Passneger lifts
A | Equipment details
1 | Machince type
2 | Reduction gear unit ratio
3 | Drive motor data
i) | KW
ii) | Starting current (Amp)
iii) | F.L. Rated current ( Amp)
iv) | Max.no. of starts per hour.
v) | Insulation class
4 | Hoist /Governor ropes (no. and size)
5 | Max. temperature tolerance during peak summer months
6 | Heat release data for machine room equipment.
B | Special Features
| Tenders to confirm Included /Not included in respect of the following | Included /Not Inclueded
1 | Auto fan off switch
2 | Fan inside the car
3 | over load warming indicator
4 | Ni.-Cd batteries with charging circuit.
5 | Pits switch
6 | Doors safety
7 | Additional weight permitted inside the car for interiors.
C | Performance parameters
1 | Leveling accuracy
2 | Governor trippring speed.

## FIRE FSYSTEM
BILL OF QUANTITY OF FIRE PROTECTION AND FIRE DETECTION / FIRE ALARM SYSTEM AT OFFICE BUILDING, BHELUPUR, VARANASI .
S.No | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
FIRE FIGHTING SYSTEM
1 | Supply & erection of ISI marked portable Fire Extinguishers, wall mounted type, wall brackets complete in all respect as per standard item with all accessories, delivery hose & nozzle wherever required, including fixing on walls as per the directions.
(MAKE : Life Guard/ Minimax / Real Value / Firex / Safex)
| ABC type 6 kg.capacity | 10 | Nos | 3650 | 36500
| CO2 gas type. 4.5 kg. Capacity | 10 | Nos | 7250 | 72500
2 | Supply, erection and testing of ISI marked M.S. pipes (Class C - heavy duty) and specials etc. (as per IS:1239) for above ground laying for hydrants and system including transportation of materials upto the worksite, cutting the pipes to required length
(MAKE : Jindal (Hissar) / Bharat / Indian Tube / Prakash)
| 100 mm dia | 42 | R.M | 1250 | 52500
| 150 mm dia | 242 | R.M | 1650 | 399300
| 80 mm dia | 18 | R.M | 950 | 17100
3 | Excavation for laying of MS pipe | 100 | R.M | 200 | 20000
4 | MS Pipe Coating and Wrapping as per IS requirement . | 100 | R.M | 400 | 40000
5 | SITC of Air release Valve with all fittings of ISI marked of approved make. | 1 | Nos. | 4000 | 4000
| Jr. Engr. | S.D.O |  | Ex. Engineer
S.No | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
6 | Supply & installation of ISI marked single headed 63 mm dia. SS Landing Valve, 80 mm dia flanged inlet with 63 mm female instantaneous outlet confirming to IS : 5290 on the fire wet riser/down comer, including making 80 NB pipe connection with riser ( Approved make) | 12 | Nos. | 7445 | 89340
7 | Supply & fixing in position ISI marked cast iron double flanged Butterfly valves with trims as per IS:13095: 1991 (PN 1 mPa) including transporting to worksite, supply & fixing nuts, bolts, gaskets & washers etc. including testing, Complete as per drawing
(MAKE : Kirloskar /Venus / IVC / Zaloto / Audco/ Sir)
| 100 MM dia | 7 | Nos | 6015 | 42105
| 80 MM dia | 8 | Nos | 5500 | 44000
8 | Supply & fixing in position ISI marked cast iron double flanged dual plate type Non Return Valves (PN 1.6 Mpa) as per IS : 5312, part - I, including transportation to worksite, supply & fixing nuts, bolts gaskets and washers etc, complete with testing as
(MAKE : Sir/ Kirloskar /Venus / IVC / Zaloto / Audco)
| 100 MM dia | 4 | Nos | 6500 | 26000
| 80 MM dia | 1 | Nos | 5600 | 5600
9 | Supply, fixing, testing & commissioning of 20 mm bore and 30 meter long hose (Rubber lined pipe as per IS:444) and hose reel for first aid fire fighting conforming to IS : 884, with 180o full swing drum, fixing brackets, 5 mm dia. shut off gun metal nozzle | 4 | Nos | 10500 | 42000
10 | Providing SS ISI marked 63 MM. dia. Instantaneous pattern short branch pipes & 16 mm dia. Nozzle suitable for interconnections to hose pipe coupling as required. (MAKE : Life Guard/ Minimax / Firex / Safex / Newage) | 12 | Nos | 2500 | 30000
| Jr. Engr. | S.D.O |  | Ex. Engineer
S.No | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
11 | Providing ISI marked RRL (IS : 636 type-II) fire hose pipe 15 meter long and 63 mm dia with ISI marked (IS : 903) gun metal male and female coupling bound and rivetted to hose pipes with copper rivets and copper wire complete as required. (MAKE:Life Guard) | 24 | Nos | 6250 | 150000
12 | Providing & fixing standard firemans axe with heavy rubber handle. | 4 | Nos | 910 | 3640
13 | Supply & installation of 2 way 63 mm instantaneous inlet for fire brigade connection and making connection with fire fighting pipe or under ground water tank and fixing inlets with caps and chains. | 1 | Nos | 10500 | 10500
14 | Providing and fixing standard fire hose cabinet double door suitable to fit in the duct made of not less than 16 SWG MS sheet and angle iron having central opening full fronted glass hinged door (4 mm thick clear glass) | 12 | Nos | 3500 | 42000
15 | Supply, Fixing, Testing & Commissioning of electrical motor driven fire pump, suitable for automatic operation consisting of following : (TERRACE PUMP 10 HP). (MAKE : Kirloskar/Mather + Platt)
(a) Horizontally mounted, Centrifugal fire pump complete for delivery of under mentioned discharge against desired mentioned head so as to ensure a minimum pressure of 30 meter at the highest and farthest outlet at the specified flow complete with necess
(b) Squirrel cage, TEFC induction motor suitable for 415 V, 3 Phase having IP 55 protection and class 'F' insulation vacuumed impregnated windings with heat and moisture resisting varnish for the above pump and flexible coupling with the pump.
(d) Suitable cement concrete pump foundation and vibration clamping arrangement as required. with foundation bolts, anti vibration pads, washers etc.
(e) Pressure switch for automatic operation of motor including necessary wiring upto control panel.
| Jr. Engr. | S.D.O |  | Ex. Engineer
S.No | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
15 | (f) Electrical Control panel with starter, 3 Pole motor protection category current limiting type MCCB, indicating light, ammeter, voltmeter, selector switches, CT's, protective fuses, single phasing protection, dry suction cut off etc. as required as per
| Discharge : 450 liter per minute | 1 | Set | 85000 | 85000
Head : 30 meter
| TOTAL ( FIRE FIGHTING SYSTEM ) |  |  |  | 1212103
FIRE DETECTION AND ALARM SYSTEM
1 | Providing, fixing, testing and commissioning of manual call points break glass type housed in 16 SWG sheet steel housing in surface/recess including making connections with wires complete in all respects and as per specifications. | 4 | Nos. | 950 | 3800
2 | Providing, fixing, testing and commissioning of electronic hooters (hooters shall also be able to work as public address system sounders) housed in 16 SWG sheet steel housing suitable for wall / ceiling and surface and recess mounting. | 4 | Nos. | 1050 | 4200
3 | Providing, fixing, testing and commissioning of smoke dector (make-system sensor). | 200 | Nos. | 1850 | 370000
4 | Providing, fixing, testing and commissioning of Response indicator (make-system sensor). | 100 | Nos. | 150 | 15000
5 | Providing, fixing, testing and commissioning of 8 zone control and indicating panel for automatic fire alarm system for detector, manual call points & hooters including stand by SMF battery & charger complete in all respect. | 1 | Set | 80000 | 80000
6 | Supply and fixing of ISI marked (IS:3419 & 2509) 2 mm thick PVC conduit in concealed / exposed system in wall, ceiling or on floor including cutting of brick work, laying of conduit and fixing it with M.S. hooks and then plastering
| 25 mm dia. conduit | 1500 | R.M | 44 | 66000
| Jr. Engr. | S.D.O |  | Ex. Engineer
S.No | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
7 | Supplying, receiving, storing, handling, fixing, wiring for fire alarm system wiring using ISI marked (IS 694) 1100 Volts grade, PVC insulated, flexible, flame retardant low smoke (FRLS), 2 x 1.5 sq. mm. copper conductor wire, drawn in existing solid / fl | 4000 | R.M | 40 | 160000
6 | Providing and fixing of self illuminated / auto glow "EXIT" signs printed on photo luminescent sheet containing self illuminated base chemical, of appropriate size not less than 400 x 150 mm, suspended from ceiling or fixed to the walls with accessories. | 8 | NOS | 1600 | 12800
| TOTAL COST ( FIRE DETECTION AND ALARM SYSTEM ) |  |  |  | 711806
FIRE PUMP HOUSE
1 | Supply, Installation, Testing and Commissioning of Diesel driven Pump 1620 lpm, 70 mtr. head. Make : Kirloskar 60 HP) with battery diesel tank and AVM pad | 1 | NOS | 450000 | 450000
2 | Supply, Installation, Testing and Commissioning of Electric Pump 1620 lpm, 70 mtr. head. Make : Kirloskar 40 HP) with AVM pad | 1 | NOS | 175000 | 175000
3 | Supply, Installation, Testing and Commissioning of Jockey Pump 180 lpm, 70 mtr. head. Make : Kirloskar 15 HP) with AVM pad | 1 | NOS | 90000 | 90000
4 | SITC of butterfly valve conforming to IS:13095, having flanged ends, with Nut, Bolt and Washers etc. as per IS:780
| a) 150 mm dia | 4 | No. | 8000 | 32000
| b) 100 mm dia | 2 | No. | 6015 | 12030
| c) 80 mm dia | 1 | No. | 5500 | 5500
5 | Supply & fixing in position ISI marked cast iron double flanged dual plate type Non Return Valves (PN 1.6 Mpa) as per IS : 5312, part - I, including transportation to worksite, supply & fixing nuts, bolts gaskets and washers etc., complete with testing as
| a) 150 mm dia | 2 | No. | 8500 | 17000
| b) 100 mm dia | 2 | No. | 6500 | 13000
| c) 80 mm dia | 1 | No. | 3600 | 3600
6 | Supply, Installation, Testing and Commissioning of Air cusion/ vessels tank. | 1 | No. | 10500 | 10500
` | Jr. Engr. | S.D.O |  | Ex. Engineer
S.No | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
7 | Supply, Installation, Testing and Commissioning of Automatic Control panel for 4 pumps. | 1 | No. | 175000 | 175000
8 | Supply, Installation, Testing and Commissioning of Pressure gauge. | 4 | No. | 2000 | 8000
9 | Supply, Installation, Testing and Commissioning of Pressure switch. | 4 | No. | 3500 | 14000
10 | Complete wiring of 4 Pumps | 1 | Job | 25000 | 25000
Note: | Rate and amount for each item shall be quoted by the tendere individually in his own hand writing both in figure and words.
Signature of Contractor
Name and Full address
………………………………………
………………………………………
…………………………………………..
| Jr. Engr. | S.D.O |  | Ex. Engineer